Abstract

Introduction

- Importance of Models for predicting Performance in partial Load

- State of the Art:  Principally Detailed Models/ Models obtained by regression on empirical data (STAFFEL). Lack of literature presence regarding the modelling in partial load, lack of information given by the manufacturer.

- Normative tends to oversimplify the real behaviour of the unit, especially considering the case the performance differs dramatically changing the operative points (maybe plot a graph of the fcop vs PLR?).

- Necessity of new uniformed standard to check the performance in partial load

Methodology

Preprocessing: STATUS Analysis.

Step for the identification of the functioning state of the different units. Considered DES conditions (power, HC, SET, LExT):

- If Pow <= 5% Pow_DES  => Unit OFF

- If T > 50 °C => DHW production (analyse the different installations sites and check if the temperature of operation is lower than 50°C, empirically chosen).

- If LExT – LET <= 1°C and AtW => Defrost. (Can be improved considering the external temperatures/ umidity?)

For AtW:

status= STAT               if Qt+1-Qt-12t≤5% HCdesACC               if Qt+1-Qt-12t>5% HCdesDECC               if Qt+1-Qt-12t<5% HCdes

For WtW:

status= STAT               if Qt+1-Qt-12t≤1% HCdesACC               if  Qt+1-Qt-12t>1% HCdesDECC               if  Qt+1-Qt-12t<1% HCdes

The reason is because the water source heat pumps tend to be more stable compared to the air to water heat pumps. Thus, there is less fluctuations on the functioning regime and the dead band can be more precise in identifying the transitory regimes. The rule is less precise with WtW machine despite the strict functioning band. Maybe there could be a better strategy to evaluate the different status conditions ( Temporal convolution analysis)

Figure 1. Time behaviour and STATUS Analysis of one AtW unit

Preprocessing: Regression on Full Load Data

Looking at the results obtained, a new regression methodology is required to improve the performance on the full load models. The full load calculation is a mandatory step in order to calculate the partial load ratio, expressed as:

|  | PLR=Qpl(SET, LExT)Qfl(SET, LExT) |  |
| --- | --- | --- |

Two linear regression models were developed to predict the full load heating capacity and the full load power:

QflQflDES=α1ΔTΔTDES+β1

WflWflDES=α2ΔTΔTDES+β2

After the first regression on catalogues data in full load, it is possible to calculates the residuals compared to the first regression. Residuals are calculated using statsmodel (I do not find how the library model works for the calculations) and then the values are used as weights (1/RES^2) for the second regression (weighted regression). The results on the final scores improves thanks to the weighted regression.

Figure 2. Pattern Behaviour with PLR filtered using the weighted linear regression for Vaillant, RIELLO.

Model for Power in partial load

The electrical power consumed by the compressor is proportional to the temperature difference between load and source (including the temperature difference between secondary fluids and the heat exchangers) and the mass flow rate of refrigerant in the circuit.

Wpl∝(ΔT+ ΔTHE,PL, mref,pl)

Wfl ∝(ΔT+ ΔTHE,fl, mref,fl)

The models can be linearly combined one with the other obtaining the following equation (imposing PLR proportional to the mass flow rate ratio):

WplWfl= α3PLR∆T+ ∆THE,pl ∆T+ ∆THE,fl+ε

WplWfl= α3PLR∆T∆T+ ∆THE,fl+β3PLR∆THE,pl∆T+ ∆THE,fl +ε

Neglecting the effect of the HE (to verify it), it is possible to write the final model:

WplWfl= α3PLR+β3PLR∆T +ε

Model for Power in partial load

The model is tested on 10 different installations with different power/ number of points per application and type of secondary fluid (two geothermal HPs). In the first phase, the models where selected considering just the catalogue for training, whereas in the second phase, the models where trained using a machine learning algorithm in order to verify the difference between the two approaches. In particular, in the second step, the dataset is divided into 80% for training and 20% for testing.

Results

The main results are showed down here:

- R2 is generally good for all the installations/ machines with few exeptions. It is around 0.5 with the operation for the unit NF2040. The catalogue of this unit present partial load points just in the conditions with LExT = 55°c which is generally too high for a real application scenario. Thus, the model tends to fail in the predictions of the SCOP and of the power. In this case, MAPE is above 20%;

- In all almost all models, the predictions are better in the stationary regime compared to the functioning considering even defrost, DHW, acceleration and deceleration are always better. The model is more precise when predicts the stationary conditions.

- The SCOP is higher in the stationary regime compare to the other. The SCOP of the geothermal HP is the highest compare to the installation ID 2050. In case of geothermal HPs, the source temperature is not related to the outdoor temperature, but to the temperature of the water – glycol mixture flowing through the evaporator.

- The models which fails the most in the prediction of the SCOP are the ones which have a lower amount of points in partial load operation.

- In order to work, the model requires at least 4 – 5 points in partial load and the corresponding points in full load (a total amount of 8 points). The points should be taken with different combinations of SET and LExT in order to cover a good part of the envelope.

- The transitory regime have an effect on the SCOP, decreasing the performance of the unit all over the periods analysed.  To predict the coefficient of performance of the unit in partial load operation during the transitory regimes, it would be necessary to analyse that specific states.

In the Figure XX, the model was trained using 80% of the experimental dataset and then tested on the remaining part.

The main differences are:

- In all the machines, the R2 is higher for the models trained with machine learning, with a range between 0.78 and 0.91 (all working conditions) compared to the dataset trained directly on the catalogue (range between 0.57 to 0.92).

- For the SCOP, the values are almost identical between the simulated values and the modelled ones with the overall operative conditions. This indicates the model is robust and performs well if it is trained with the correct amount of data which space inside the overall range of work of the compressor.

- The R2 for the VA+ are very similar, with differences lower than 7% in every case.

- The R2 for the Riello NXHM is similar, with differences lower than 10% in every case.

- For NIBE F2040, the maximum difference is around 30%. This machine is the one that performs worse compared to the case trained with the Machine Learning approach. The reason is the training dataset: this machine has as training points in partial load working conditions with LExT equals to 55°C. This condition is never reached in the real operation of the unit (with the exeption of the DHW generation) since the desing temperature for this installation is 45°C.

- For the Geothermal Heat Pump MT AQ30I, the maximum difference is around 12%. The R2 is not so high compared to the Air to Water units. Even in this case, the reason could be related to the working points. Indeed, for the vast majority of time, the unit performs at termperatures which are lower than 45°C but also lower than 35°C. This can lead the training on the wrong fitting, decreasing the performance of the machine.